## Typical values
Typical heat per unit for each equipment type and size. Fill the four W columns (blank = not filled yet; 0 is a real zero) and the Source (https link). Under-hood columns are for cooking only; leave them blank elsewhere. Keep Typical IDs unchanged; add new rows with the next unused ID.
Typical ID | Equipment type | Size band | How to tell the size from the drawings | Matching aliases (semicolon separated) | Generic fallback for type | Sensible W per unit (free-standing) | Latent W per unit (free-standing) | Sensible W per unit (under a hood) | Latent W per unit (under a hood) | Use pattern | Heat rejection location | Based on (catalogue IDs) | Source | Reviewed by | Reviewed on | Notes
TV-0001 | Under-bench fridge | 1-door | Up to about 0.9 m wide, or labelled 1DR | UB fridge;UBR;under bench fridge;under counter fridge;underbench refrigerator;UBR 1DR;underbench fridges;under-bench fridges |  | 40.833 | 0 |  |  | CONTINUOUS | Integral air-cooled refrigeration in this room; net 24-h heat |  | https://www.bromicrefrigeration.com.au/wp-content/uploads/2023/08/UBC0140SD-NR_SPEC_0723.pdf | Codex (needs partner review) | 2026-10-20 | Bromic UBC0140SD-NR (138 L, 1 door); manufacturer's Specifications, Energy Consumption (kWh/24h): 0.98. Median of 1 example(s): 40.83–40.83 W; kWh/day ×1000/24. Net room heat equals average electrical consumption for integral same-room refrigeration; NOT condenser gross rejection, cooling capacity or nameplate input. Latent 0: no uncaptured evaporative source. 24-h average, not a compressor peak. Single-product analogue; band not independently validated.
TV-0002 | Under-bench fridge | 2-door | About 0.9–1.5 m wide, or labelled 2DR | UB fridge 2 door;UBR 2DR;2 door underbench fridge;2DR;2DR UBR;2 door underbench refrigerator |  | 138.833 | 0 |  |  | CONTINUOUS | Integral air-cooled refrigeration in this room; net 24-h heat |  | https://www.bromicrefrigeration.com.au/product/under-bench-fridge-282l-2-doors-stainless-steel/ | Codex (needs partner review) | 2026-10-20 | Bromic UBC1360SD-NR / UBC1360GD-NR (282 L, 2 doors); manufacturer's Specifications, Energy Consumption (kWh/24h): 3.024, 3.64. Median of 2 example(s): 126.00–151.67 W; kWh/day ×1000/24. Net room heat equals average electrical consumption for integral same-room refrigeration; NOT condenser gross rejection, cooling capacity or nameplate input. Latent 0: no uncaptured evaporative source. 24-h average, not a compressor peak. One-brand sample; not market validation. Other sources: https://www.bromicrefrigeration.com.au/wp-content/uploads/2023/08/UBC1360GD-NR_SPEC_0723.pdf
TV-0003 | Under-bench fridge | 3-door | Over about 1.5 m wide, or labelled 3DR | UB fridge 3 door;UBR 3DR;3 door underbench fridge;3DR;3DR UBR |  | 139.208 | 0 |  |  | CONTINUOUS | Integral air-cooled refrigeration in this room; net 24-h heat |  | https://www.bromicrefrigeration.com.au/product/under-bench-fridge-417l-3-doors-stainless-steel/ | Codex (needs partner review) | 2026-10-20 | Bromic UBC1795SD-NR (417 L, 3 doors); manufacturer's Specifications, Energy Consumption (kWh/24h): 3.341. Median of 1 example(s): 139.21–139.21 W; kWh/day ×1000/24. Net room heat equals average electrical consumption for integral same-room refrigeration; NOT condenser gross rejection, cooling capacity or nameplate input. Latent 0: no uncaptured evaporative source. 24-h average, not a compressor peak. Single-product analogue; band not independently validated.
TV-0004 | Under-bench freezer | Any |  | UB freezer;UBF;under bench freezer;underbench freezer;underbench freezers |  | 333.75 | 0 |  |  | CONTINUOUS | Integral air-cooled refrigeration in this room; net 24-h heat |  | https://www.bromicrefrigeration.com.au/wp-content/uploads/2023/08/UBF1360SD-NR_SPEC_0824.pdf | Codex (needs partner review) | 2026-10-20 | Bromic UBF0140SD-NR / UBF1360SD-NR / UBF1795SD-NR (115–417 L); manufacturer's Specifications, Energy Consumption (kWh/24h): 1.65, 8.01, 9.111. Median of 3 example(s): 68.75–379.62 W; kWh/day ×1000/24. Net room heat equals average electrical consumption for integral same-room refrigeration; NOT condenser gross rejection, cooling capacity or nameplate input. Latent 0: no uncaptured evaporative source. 24-h average, not a compressor peak. One-brand sample; not market validation. Other sources: https://www.bromicrefrigeration.com.au/wp-content/uploads/2023/08/UBF0140SD-NR_SPEC_0324.pdf ; https://www.bromicrefrigeration.com.au/product/under-bench-freezer-3-doors-stainless-steel/
TV-0005 | Upright fridge | 1-door | Up to about 0.8 m wide | upright fridge;reach in fridge;1 door fridge;single door fridge |  | 82.5 | 0 |  |  | CONTINUOUS | Integral air-cooled refrigeration in this room; net 24-h heat |  | https://www.bromicrefrigeration.com.au/product/upright-display-fridge-372l-1-door-flat-glass/ | Codex (needs partner review) | 2026-10-20 | Bromic GM0374-NR (372 L, 1 glass door); manufacturer's Specifications, Energy Consumption (kWh/24h): 1.98. Median of 1 example(s): 82.50–82.50 W; kWh/day ×1000/24. Net room heat equals average electrical consumption for integral same-room refrigeration; NOT condenser gross rejection, cooling capacity or nameplate input. Latent 0: no uncaptured evaporative source. 24-h average, not a compressor peak. Single-product analogue; band not independently validated. Glass-door analogue for this broad band; verify solid-door kitchen unit separately.
TV-0006 | Upright fridge | 2-door | Over about 0.8 m wide | 2 door fridge;double door fridge;2 door upright fridge |  | 285.833 | 0 |  |  | CONTINUOUS | Integral air-cooled refrigeration in this room; net 24-h heat |  | https://www.bromicrefrigeration.com.au/wp-content/uploads/2023/08/GM1000LWCAS_SPEC_0723.pdf | Codex (needs partner review) | 2026-10-20 | Bromic GM1000LWCAS (960 L, 2 glass doors); manufacturer's Specifications, Energy Consumption (kWh/24h): 6.86. Median of 1 example(s): 285.83–285.83 W; kWh/day ×1000/24. Net room heat equals average electrical consumption for integral same-room refrigeration; NOT condenser gross rejection, cooling capacity or nameplate input. Latent 0: no uncaptured evaporative source. 24-h average, not a compressor peak. Single-product analogue; band not independently validated. Glass-door analogue; not a 1300 L solid-door model.
TV-0007 | Upright freezer | Any |  | upright freezer;reach in freezer;upright freezers |  | 210.062 | 0 |  |  | CONTINUOUS | Integral air-cooled refrigeration in this room; net 24-h heat |  | https://www.bromicrefrigeration.com.au/wp-content/uploads/2025/06/UF0650SDF-NR_SPEC_0525.pdf | Codex (needs partner review) | 2026-10-20 | Bromic UF0374SDS-NR / UF0650SDF-NR (300 / 650 L); manufacturer's Specifications, Energy Consumption (kWh/24h): 1.823, 8.26. Median of 2 example(s): 75.96–344.17 W; kWh/day ×1000/24. Net room heat equals average electrical consumption for integral same-room refrigeration; NOT condenser gross rejection, cooling capacity or nameplate input. Latent 0: no uncaptured evaporative source. 24-h average, not a compressor peak. One-brand sample; not market validation. Other sources: https://www.bromicrefrigeration.com.au/product/upright-freezer-300l-1-door-solid/
TV-0008 | Chest freezer | Any |  | chest freezer;chest freezers |  | 93.167 | 0 |  |  | CONTINUOUS | Integral air-cooled refrigeration in this room; net 24-h heat |  | https://www.bromicrefrigeration.com.au/product/display-chest-freezer-296l-flat-glass-top/ | Codex (needs partner review) | 2026-10-20 | Bromic CF0300FTFG-NR (296 L, glass top); manufacturer's Specifications, Energy Consumption (kWh/24h): 2.236. Median of 1 example(s): 93.17–93.17 W; kWh/day ×1000/24. Net room heat equals average electrical consumption for integral same-room refrigeration; NOT condenser gross rejection, cooling capacity or nameplate input. Latent 0: no uncaptured evaporative source. 24-h average, not a compressor peak. Single-product analogue; band not independently validated. Glass-top analogue; not a generic domestic chest freezer.
TV-0009 | Refrigerated display cabinet | Up to 1.2 m | Up to about 1.2 m long | display fridge;display chiller;cold display;refrigerated display;deli display |  | 570.208 | 0 |  |  | CONTINUOUS | Integral air-cooled refrigeration in this room; net 24-h heat |  | https://www.bromicrefrigeration.com.au/product/cake-display-1200mm/ | Codex (needs partner review) | 2026-10-20 | Bromic FD4T0900C-NR / FD4T1200C-NR (900 / 1200 mm enclosed cake cases); manufacturer's Specifications, Energy Consumption (kWh/24h): 12.5, 14.87. Median of 2 example(s): 520.83–619.58 W; kWh/day ×1000/24. Net room heat equals average electrical consumption for integral same-room refrigeration; NOT condenser gross rejection, cooling capacity or nameplate input. Latent 0: no uncaptured evaporative source. 24-h average, not a compressor peak. One-brand sample; not market validation. Not an open multideck. Other sources: https://www.bromicrefrigeration.com.au/product/cake-display-900mm/
TV-0010 | Refrigerated display cabinet | Over 1.2 m | Over about 1.2 m long | display fridge;display chiller;cold display;refrigerated display;deli display |  | 776.25 | 0 |  |  | CONTINUOUS | Integral air-cooled refrigeration in this room; net 24-h heat |  | https://www.bromicrefrigeration.com.au/product/cake-display-1500mm/ | Codex (needs partner review) | 2026-10-20 | Bromic FD4T1500C-NR (1500 mm enclosed cake case); manufacturer's Specifications, Energy Consumption (kWh/24h): 18.63. Median of 1 example(s): 776.25–776.25 W; kWh/day ×1000/24. Net room heat equals average electrical consumption for integral same-room refrigeration; NOT condenser gross rejection, cooling capacity or nameplate input. Latent 0: no uncaptured evaporative source. 24-h average, not a compressor peak. Single-product analogue; band not independently validated. Not an open multideck or an arbitrary length.
TV-0011 | Drinks fridge | Glass door | Single glass door drinks fridge; multi-door is TV-0066 | drinks fridge;bottle cooler;beverage fridge;glass door fridge;single door drinks fridge;drinks refrigerator |  | 82.5 | 0 |  |  | CONTINUOUS | Integral air-cooled refrigeration in this room; net 24-h heat |  | https://www.bromicrefrigeration.com.au/product/upright-display-fridge-372l-1-door-flat-glass/ | Codex (needs partner review) | 2026-10-20 | Bromic GM0374-NR (372 L, 1 glass door); manufacturer's Specifications, Energy Consumption (kWh/24h): 1.98. Median of 1 example(s): 82.50–82.50 W; kWh/day ×1000/24. Net room heat equals average electrical consumption for integral same-room refrigeration; NOT condenser gross rejection, cooling capacity or nameplate input. Latent 0: no uncaptured evaporative source. 24-h average, not a compressor peak. Single-product analogue; band not independently validated. Single-door only; multi-door analogues are TV-0066.
TV-0012 | Refrigerated prep bench | Any |  | prep fridge;refrigerated prep bench;saladette;pizza prep fridge |  | 162.083 | 0 |  |  | CONTINUOUS | Integral air-cooled refrigeration in this room; net 24-h heat |  | https://www.bromicrefrigeration.com.au/wp-content/uploads/2025/06/PP1700_SPEC_0525.pdf | Codex (needs partner review) | 2026-10-20 | Bromic PP1700 (572 L, 2 doors, 9 pans); manufacturer's Specifications, Energy Consumption (kWh/24h): 3.89. Median of 1 example(s): 162.08–162.08 W; kWh/day ×1000/24. Net room heat equals average electrical consumption for integral same-room refrigeration; NOT condenser gross rejection, cooling capacity or nameplate input. Latent 0: no uncaptured evaporative source. 24-h average, not a compressor peak. Single-product analogue; band not independently validated. Closed pan lids per test; service loading can increase heat. EQ-0322 is idle-only, not a daily average.
TV-0013 | Ice machine | Up to 150 kg/day | Printed output up to 150 kg/day, or not printed | ice machine;ice maker;IM;ice flaker;ice machines;ice makers |  | 923.174 | 0 |  |  | WHILE_OPEN | Integral air-cooled condenser in room; ice-making heat rejection |  | https://www.hoshizakiamerica.com/product/km-301baj/ | Codex (needs partner review) | 2026-10-20 | Hoshizaki KM-116BAJ / KM-301BAJ (57 / 132 kg/day); published Heat Rejection, [2100, 4200] BTU/h ×0.29307107. Median 2 example(s), 615.4–1230.9 W. Gross sensible rejection of integral air-cooled condenser while making ice, NOT daily input. Latent 0 assumes closed machine, plumbed drains, no room evaporation; no remote/water-cooled condenser. US 115 V/60 Hz historical analogues; Australian installed model and capacity need partner review. WHILE_OPEN because not a 24-h average. Other source: https://www.hoshizakiamerica.com/product/km-116baj/
TV-0014 | Ice machine | Over 150 kg/day | Printed output over 150 kg/day | ice machine;ice maker;IM;ice machines;ice makers |  | 2051.497 | 0 |  |  | WHILE_OPEN | Integral air-cooled condenser in room; ice-making heat rejection |  | https://www.hoshizakiamerica.com/product/km-515maj/ | Codex (needs partner review) | 2026-10-20 | Hoshizaki KM-515MAJ (239 kg/day); published Heat Rejection, [7000] BTU/h ×0.29307107. Median 1 example(s), 2051.5–2051.5 W. Gross sensible rejection of integral air-cooled condenser while making ice, NOT daily input. Latent 0 assumes closed machine, plumbed drains, no room evaporation; no remote/water-cooled condenser. US 115 V/60 Hz historical analogues; Australian installed model and capacity need partner review. WHILE_OPEN because not a 24-h average.
TV-0015 | Blast chiller | Any |  | blast chiller;blast freezer | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0313 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. No sourced normal-cycle heat-to-room sensible/latent split for this size-free blast-chiller band; pull-down, load and condenser location matter. Refrigeration capacity and rated input are not room gains. EQ-0313 is reference-only.
TV-0016 | Deep fryer | Countertop | Bench-mounted | fryer;deep fryer;countertop fryer;deep fryers;fryers |  | 694 | 1629 | 202 | 0 | WHILE_OPEN | Room; under-hood values require complete capture exhausted outdoors | EQ-0169 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | ASHRAE 2017 Fundamentals ch18 Table 5B, countertop open deep-fat fryer: use measured heat columns (sensible = radiant + convective), not rated/cooking input. One test analogue; size-band and installed duty need partner review. FU=0.83 is already reflected in test emissions; do not multiply it again. Under-hood sensible = tabulated radiant 202 W, latent 0, per ch18 effective capture principle; this is a derived capture estimate, not a separate hooded test. Recirculating/ineffective hoods use free-standing values.
TV-0017 | Deep fryer | Floor-standing | Free-standing, single or twin pan | fryer;deep fryer;floor fryer;twin pan fryer;pressure fryer;deep fryers;fryers |  |  |  | 293 | 0 | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0310 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. EQ-0310 / Tables 5C–5D are hooded idle/ready examples, not free-standing cooking data. No matching floor fryer unhooded sensible/latent measurements located; countertop values are not scaled by input.
TV-0018 | Griddle / hotplate | Up to 0.9 m | Up to about 0.9 m wide | griddle;hotplate;hot plate;flat top;griddles;hotplates |  | 1479 | 1277 | 848 | 0 | WHILE_OPEN | Room; under-hood values require complete capture exhausted outdoors | EQ-0170 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | ASHRAE 2017 Fundamentals ch18 Table 5B, countertop griddle (848 +631 sensible; published component rounding differs from EQ-0170 by 1 W): use measured heat columns (sensible = radiant + convective), not rated/cooking input. One test analogue; size-band and installed duty need partner review. FU=0.41 is already reflected in test emissions; do not multiply it again. Under-hood sensible = tabulated radiant 848 W, latent 0, per ch18 effective capture principle; this is a derived capture estimate, not a separate hooded test. Recirculating/ineffective hoods use free-standing values.
TV-0019 | Griddle / hotplate | Over 0.9 m | Over about 0.9 m wide | griddle;hotplate;hot plate;flat top | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0170 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. Hooded 900 mm examples do not establish unhooded emissions or performance above 0.9 m. No width-scaled nameplate substitution.
TV-0020 | Chargrill | Any |  | chargrill;char grill;grill |  |  |  | 3165 | 0 | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0309 | https://handbook.ashrae.org/Handbooks/F25/SI/F25_Ch18/F25_Ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. Table 8C 900 mm electric underfired broiler gives hooded idle radiation only; gas/charcoal differ. No comparable unhooded sensible/latent test.
TV-0021 | Combi oven | 6-tray | 6-1/1 or 6-2/1, or not printed | combi oven;combi;combi steamer;combination oven | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0302 | https://www.moffat.com.au/sites/default/files/products/specification/OES_6_10_MINI_MOBILE_AN.pdf | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. EQ-0302 publishes 402.78 W sensible /369.44 W latent for OES 6.10 mini, but test mode/exhaust and radiation split are unspecified. Cannot supply defensible free-standing AND hooded pair for this band.
TV-0022 | Combi oven | 10-tray or larger | 10-1/1 and larger | combi oven 10 tray;10 tray combi | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0302 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. No 10-tray-or-larger unhooded emissions located. The 6-tray mini is not size-scaled; Tables 5C–5D supply hooded idle examples only.
TV-0023 | Convection oven | Any |  | convection oven;convection ovens;fan forced oven |  |  |  | 440 | 0 | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0156 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. EQ-0156 / Table 5C full-size convection oven: 440 W hooded idle radiation only. No unhooded sensible/latent data located; conveyor/pizza tests are different types.
TV-0024 | Range / cooktop | 4-burner |  | 4 burner;four burner range;cooktop;stove | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0154; EQ-0308 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. Table 5B single hotplate is not a four-burner range; Table 5C has 3/6 elements at idle under a hood only. No four-burner unhooded sensible/latent test located.
TV-0025 | Range / cooktop | 6-burner |  | 6 burner;six burner range;range;oven range |  |  |  | 4074 | 0 | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0308 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. Table 5C six-element range (oven off) 4074 W is hooded idle radiation only. No matching six-burner free-standing sensible/latent split located.
TV-0026 | Wok burner | Per burner | Count each wok hole | wok;wok burner;wok range |  |  |  | 1524 | 0 | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination |  | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. Table 5D wok 1524 W is hooded idle radiation, not free-standing burner heat. No unhooded sensible/latent data or per-burner test located.
TV-0027 | Induction hob | Per hob |  | induction;induction hob;induction cooktop;induction hobs |  | 318 | 335 | 0 | 0 | WHILE_OPEN | Room; under-hood values require complete capture exhausted outdoors | EQ-0153; EQ-0307 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | ASHRAE 2017 Fundamentals ch18 Table 5B, one countertop induction hob: use measured heat columns (sensible = radiant + convective), not rated/cooking input. One test analogue; size-band and installed duty need partner review. FU=0.13 is already reflected in test emissions; do not multiply it again. Under-hood sensible = tabulated radiant 0 W, latent 0, per ch18 effective capture principle; this is a derived capture estimate, not a separate hooded test. Recirculating/ineffective hoods use free-standing values.
TV-0028 | Salamander | Any |  | salamander;salamander grill |  |  |  | 2051 | 0 | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0306 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. EQ-0306 / Table 5C electric salamander: 2051 W hooded idle radiation only. No comparable unhooded cooking heat split located. Cheesemelter is not automatically a salamander.
TV-0029 | Bain-marie / food well | Any |  | bain marie;bain-marie;food well;steam table;hot food well;bain maries;food wells |  | 264 | 762 | 88 | 0 | WHILE_OPEN | Room; hood values only for effective externally exhausted capture | EQ-0312 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | ASHRAE 2017 ch18 Table 5A / EQ-0312 two-well steam table at holding temperature (idle/ready, NOT reheat/startup). Normal maintaining/holding analogue only; single test. Sensible 88+176=264 W, latent 762 W. FU 0.69 already in measurements. Under effective external hood use radiant 88 W and latent 0 (derived capture estimate). Number/size of wells and actual steam release need review. No electrical nameplate used.
TV-0030 | Heated display / holding cabinet | Any |  | hot food display;heated display;warmer;hot holding cabinet;food warmer |  | 762.5 | 0 | 234.5 | 0 | WHILE_OPEN | Room; hood values only for effective externally exhausted capture | EQ-0167; EQ-0168; EQ-0311 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | ASHRAE 2017 ch18 Table 5A, four holding examples: insulated/uninsulated hot-serving cabinets and dry/moist hot-food cases. Component medians S=762.5 W (352–1026), L=0 W (0–176); not a measured single cabinet. Normal temperature-maintaining state only, not reheating. Radiant median=234.5 W (117,205,264,264), used under an effective external hood with L=0. Mixed insulation/moisture sample; partner must review latent when wet holding is known. FU already in table, not applied again.
TV-0031 | Rice cooker | Any |  | rice cooker |  | 109 | 44 | 14 | 0 | WHILE_OPEN | Room; under-hood values require complete capture exhausted outdoors | EQ-0304 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | ASHRAE 2017 Fundamentals ch18 Table 5B, rice cooker: use measured heat columns (sensible = radiant + convective), not rated/cooking input. One test analogue; size-band and installed duty need partner review. FU=0.75 is already reflected in test emissions; do not multiply it again. Under-hood sensible = tabulated radiant 14 W, latent 0, per ch18 effective capture principle; this is a derived capture estimate, not a separate hooded test. Recirculating/ineffective hoods use free-standing values.
TV-0032 | Pasta cooker | Any |  | pasta cooker;noodle cooker |  |  |  | 0 | 0 | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0305 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. Pasta cookers in Tables 5C–5D have zero hooded idle radiation, but no unhooded sensible/latent values. Zero captured radiation does not prove zero free-standing load.
TV-0033 | Microwave | Commercial |  | microwave;commercial microwave;microwaves |  | 934 | 995 | 0 | 0 | WHILE_OPEN | Room; under-hood values require complete capture exhausted outdoors | EQ-0303 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | ASHRAE 2017 Fundamentals ch18 Table 5B, commercial microwave: use measured heat columns (sensible = radiant + convective), not rated/cooking input. One test analogue; size-band and installed duty need partner review. FU=1.39 as published (not an electrical efficiency) is already reflected in test emissions; do not multiply it again. Under-hood sensible = tabulated radiant 0 W, latent 0, per ch18 effective capture principle; this is a derived capture estimate, not a separate hooded test. Recirculating/ineffective hoods use free-standing values.
TV-0034 | Toaster | Any |  | toaster;conveyor toaster;toasters |  | 895 | 322 | 180 | 0 | WHILE_OPEN | Room; hood values only for effective externally exhausted capture | EQ-0150 | https://handbook.ashrae.org/Handbooks/F25/SI/F25_Ch18/F25_Ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | ASHRAE 2025 ch18 Tables 8A–8B: cooking pop-up 4-slice, vertical contact, small conveyor. Component medians: sensible 895 W (469–1332), latent 322 W (293–373), radiant 180 W (59–358). Under effective external hood use radiant median 180 and L=0 (derived capture estimate). Three test types, not one product; large conveyor excluded. FU 0.49/0.71/0.98 already represented, not reapplied. Broad band needs subtype review.
TV-0035 | Sandwich press | Any |  | sandwich press;panini grill;contact grill;sandwich presses |  | 913 | 150 | 195 | 0 | WHILE_OPEN | Room; under-hood values require complete capture exhausted outdoors | EQ-0151 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | ASHRAE 2017 Fundamentals ch18 Table 5B, panini grill (195 +718 =913 sensible; EQ-0151 uses rounded total-minus-latent 912): use measured heat columns (sensible = radiant + convective), not rated/cooking input. One test analogue; size-band and installed duty need partner review. FU=0.76 is already reflected in test emissions; do not multiply it again. Under-hood sensible = tabulated radiant 195 W, latent 0, per ch18 effective capture principle; this is a derived capture estimate, not a separate hooded test. Recirculating/ineffective hoods use free-standing values.
TV-0036 | Dishwasher | Pass-through / hood type |  | dishwasher;pass through dishwasher;hood type dishwasher;warewasher;DW;dishwashers |  | 1685 | 5626 |  |  | WHILE_OPEN | Unhooded dishwashing room; hot drain-water energy excluded |  | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | ASHRAE 2017 ch18 Table 5F, unhooded door-type washing, hot-water and chemical sanitizing (without heat recovery). Component medians S=1685 W (1143–2227), L=5626 W (3868–7384). Hood-type here means the machine lifting door, not an extracting canopy. No external capture credited. Two test analogues, not connected ratings. Actual cycles/h, heat recovery and exhaust are major reviewer checks; table FU 0.31/0.52 not reapplied.
TV-0037 | Dishwasher | Under-counter |  | under counter dishwasher;undercounter dishwasher;DW;dishwashers;underbench dishwasher |  | 1172.28 | 1348.13 |  |  | WHILE_OPEN | Unhooded dishwashing room; hot drain-water energy excluded | EQ-0157 | https://www.hobartcorp.com/sites/default/files/webdam-assets/LXeH%20High%20Temp%20Undercounter%20Dishwasher%20Spec%20Sheet%20F40902%20(09-22).pdf | Codex (needs partner review) | 2026-10-20 | EQ-0157: Hobart LXeH F40902 (09/22), p2 Heat Output: sensible 4000 BTU/h, latent 4600 BTU/h ×0.29307107. Catalogue rounded values retained. Published capacity 32 racks/h; specific manufacturer analogue, not universal domestic/undercounter heat. No 6.7 kW connected-load substitution; no external capture credited. Confirm actual duty, heat recovery, supply-water temperature and 50 Hz variant.
TV-0038 | Glasswasher | Any |  | glasswasher;glass washer;GW;glass washers;glasswashers |  | 1400 | 700 |  |  | WHILE_OPEN | Unhooded wash room; no remote moisture capture credited | EQ-0320 | https://partnernet.meiko-global.com/download/2177/en | Codex (needs partner review) | 2026-10-20 | EQ-0320: MEIKO M-iClean UM, technical data p15 (20 programme runs/h): 1.4 kW sensible, 0.7 kW latent; ×1000 W/kW heat output, NOT electrical load. Single-model analogue; confirm cycles/h, recovery and actual model. Exhaust not credited. Factory-connected load is separate and must not be added.
TV-0039 | Espresso machine | 2-group |  | coffee machine;espresso machine;2 group coffee machine;espresso machines;coffee machines | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0147 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. EQ-0147 / Table 5A espresso example is idle/ready 352 W (rounded); group count and brewing steam-duty are unspecified. No supported distinction between 2-group and 3+-group normal-service emissions.
TV-0040 | Espresso machine | 3-group or larger |  | 3 group coffee machine;espresso machine 3 group;espresso machines;coffee machines | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0147 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. EQ-0147 / Table 5A espresso example is idle/ready 352 W (rounded); group count and brewing steam-duty are unspecified. No supported distinction between 2-group and 3+-group normal-service emissions.
TV-0041 | Coffee grinder | Any |  | coffee grinder;grinder;coffee grinders |  | 73 | 0 |  |  | WHILE_OPEN | Room, dry grinder; no exported process heat credited |  | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | ASHRAE 2017 ch18 Table 10: coffee grinder up to 12 cups, measured 15-min peak heat 73 W. Small dry-grinder analogue only, NOT EQ-0319 440 W nominal rating or a validated commercial espresso grinder. Latent 0 assumes no moisture process. Use actual grinding duty; 73 W has not been multiplied by another arbitrary duty factor. Single tested appliance, high uncertainty for large grinders.
TV-0042 | Hot water boiler / urn | Any |  | hot water unit;boiling water unit;zip;urn;boiler;hot water urn;boiling water urn | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0149 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. EQ-0149 / Table 5A is a coffee-brewing urn at idle (147 W sensible /205 W latent), not a normal-service sealed hot-water boiler. Need model, venting, draw-off and room emissions; rated heating kW is not room gain.
TV-0043 | Blender / food processor | Any |  | blender;food processor | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0166 | https://loipart.com/en/product/food-processor-55-l | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. Loipart K55 page opened: 1.3 kW electrical loading only, no numerical heat emission. EQ-0166 is an electrical operating rating, not measured room heat; no supported design-hour sensible/latent split.
TV-0044 | Dough mixer | Any |  | dough mixer;planetary mixer;mixer;dough mixers |  | 480 | 0 |  |  | WHILE_OPEN | Mixer in room; dry operation, no external exhaust |  | https://loipart.com/en/product/planetary-mixer-20-l-with-hub-table-type-3810 | Codex (needs partner review) | 2026-10-20 | Loipart LMX20 20 L /6.8 kg planetary mixer, Technical Product Specifications: Heat Emission 0.48 kW ×1000 =480 W; not its 0.6 kW loading. Dry dough-mixing analogue: all published emission treated sensible, latent 0 assumes no steam/evaporation. Single product, not a large spiral mixer; production-capacity band and intermittent duty need partner review.
TV-0045 | Food slicer | Any |  | slicer;meat slicer;food slicer | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0318 | https://trespade.com/en/products/d-250-professional-slicer | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. EQ-0318 is published electrical consumption (140 W), not a measured heat-to-room design-hour value. Need actual operating heat/duty and food heat export. No nameplate substitution.
TV-0046 | Ice cream / frozen dessert machine | Any |  | ice cream machine;soft serve;gelato machine;frozen yoghurt machine | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination | EQ-0324 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. No sourced normal-service heat-to-room split for this broad ice-cream/frozen-dessert machine type. Condenser may be air/water/remote; electrical rating or freezing capacity is not a defensible room heat value.
TV-0047 | POS terminal | Any |  | POS;point of sale;register;EFTPOS;cash register;POS terminals;point of sale terminal |  | 58 | 0 |  |  | WHILE_OPEN | Electronics and integral display in room | EQ-0029 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | EQ-0029 / ASHRAE 2017 ch18 Table 10 touchscreen computer/POS: measured 15-min peak heat 58 W. One historical 380 mm touchscreen system, not current-market validation. Includes its screen; do not add a separate monitor for an integrated terminal. Dry electronics, latent 0; room heat assumed retained.
TV-0048 | Desktop computer | Medium | Ordinary office desktop | computer;PC;desktop;CPU;desktop computers;PCs |  | 80 | 0 |  |  | WHILE_OPEN | Desktop electronics in room; monitor counted separately |  | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | ASHRAE 2017 ch18 Table 8A desktop test configurations, median of 21 listed 15-min peak heat measurements: 80 W, range 26–151 W. Equal weight per listed test configuration, not sample-count weighted. Tower only, excludes monitor. Dry electronics latent 0. Historical office-size analogue; gaming/workstation/server devices excluded.
TV-0049 | Monitor | Up to 27 inch |  | monitor;screen;monitors |  | 22 | 0 |  |  | WHILE_OPEN | Display in room; no second count of integrated screen |  | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | ASHRAE 2017 ch18 Table 8D, nine listed screen configurations 546–686 mm (21.5–27 inch), median measured peak 22 W, range 14–26 W; atypical 34/50/55 inch excluded. Dry display, latent 0. Historical LED screen sample; brightness matters. Do not count separately if included in a POS/all-in-one.
TV-0050 | TV / digital screen | Up to 55 inch |  | TV;television;digital screen;menu board;display screen;TVs;televisions;digital screens |  | 87.042 | 0 |  |  | WHILE_OPEN | Indoor display and integrated supply in room |  | https://media.us.lg.com/m/1d6bfab4849f227a/original/UH5N-M-Series-Spec-Sheet.pdf | Codex (needs partner review) | 2026-10-20 | LG UH5N-M specification SPEC_UH5N-M_0625_5.0A p4, Heat Dissipation (Typ.), models 43 /49 /55UH5N-M: [283, 297, 351] BTU/h ×0.29307107. Median of 3 models; sensible range 82.9–102.9 W. One manufacturer; 500-nit commercial display analogue, not all consumer TVs. Dry electronics latent 0. No maximum/nameplate input substituted; installed brightness and size beyond sampled band need review.
TV-0051 | TV / digital screen | Over 55 inch |  | TV;television;digital screen;video wall;TVs;televisions;digital screens |  | 160.017 | 0 |  |  | WHILE_OPEN | Indoor display and integrated supply in room |  | https://media.us.lg.com/m/1d6bfab4849f227a/original/UH5N-M-Series-Spec-Sheet.pdf | Codex (needs partner review) | 2026-10-20 | LG UH5N-M specification SPEC_UH5N-M_0625_5.0A p4, Heat Dissipation (Typ.), models 65 /75 /86UH5N-M: [444, 546, 699] BTU/h ×0.29307107. Median of 3 models; sensible range 130.1–204.9 W. One manufacturer; 500-nit commercial display analogue, not all consumer TVs. Dry electronics latent 0. No maximum/nameplate input substituted; installed brightness and size beyond sampled band need review.
TV-0052 | Illuminated sign / lightbox | Per sign |  | sign;illuminated sign;lightbox;light box;neon | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination |  | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. No defensible W per sign without sign dimensions, illuminated area, technology and indoor heat destination. ASHRAE lighting method needs actual operating lighting power; a power allowance or one exit sign is not an advertising lightbox typical. Avoid double-counting lighting.
TV-0053 | Printer | Small office |  | printer;receipt printer;label printer |  | 66 | 0 |  |  | WHILE_OPEN | Printer in room; no separate heat credit for paper export |  | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | ASHRAE 2017 ch18 Table 9: small-office desktop multifunction (56 W) and small-office lasers (89/67/65 W), median 66 W, range 56–89 W of measured 15-min peak heat, not nameplate. Four normal printing examples. Dry electronics latent 0; excludes industrial plotters/copiers. Printer diversity 45% is separately listed in Table 11; not pre-applied here.
TV-0054 | Any cooking appliance | Generic | Used only when no row above fits |  | cooking | 762.5 | 335 | 180 | 0 | WHILE_OPEN | In room; generic cannot establish installed heat destination | TV-0016; TV-0018; TV-0027; TV-0029; TV-0030; TV-0031; TV-0033; TV-0034; TV-0035 | https://handbook.ashrae.org/Handbooks/F25/SI/F25_Ch18/F25_Ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Component-wise medians of 9 filled cooking rows (TV-0016, TV-0018, TV-0027, TV-0029, TV-0030, TV-0031, TV-0033, TV-0034, TV-0035): S=762.5 W, L=335 W. Equal weight per typical row; component medians need not describe one appliance. Range S=109–1479, L=0–1629 W. Representative source: TV-0034. Broad fallback only; partner review required. Hood S is median radiation; L=0 requires effective outdoor exhaust. Runtime generic branch currently uses free-standing fields.
TV-0055 | Any refrigerated unit | Generic | Used only when no row above fits |  | refrigeration | 162.083 | 0 |  |  | CONTINUOUS | Integral same-room refrigeration, net 24-h average | TV-0001; TV-0002; TV-0003; TV-0004; TV-0005; TV-0006; TV-0007; TV-0008; TV-0009; TV-0010; TV-0011; TV-0012; TV-0066 | https://www.bromicrefrigeration.com.au/wp-content/uploads/2025/06/PP1700_SPEC_0525.pdf | Codex (needs partner review) | 2026-10-20 | Component-wise medians of 13 filled refrigeration rows (TV-0001, TV-0002, TV-0003, TV-0004, TV-0005, TV-0006, TV-0007, TV-0008, TV-0009, TV-0010, TV-0011, TV-0012, TV-0066): S=162.083 W, L=0 W. Equal weight per typical row; component medians need not describe one appliance. Range S=40.833–776.25, L=0–0 W. Representative source: TV-0012. Broad fallback only; partner review required. Only 24-h net integral storage/cabinet rows; active ice-machine rejection excluded. Not valid for remote/water-cooled heat rejection.
TV-0056 | Any dishwasher | Generic | Used only when no row above fits |  | dishwashing | 1400 | 1348.13 |  |  | WHILE_OPEN | In room; generic cannot establish installed heat destination | TV-0036; TV-0037; TV-0038 | https://www.hobartcorp.com/sites/default/files/webdam-assets/LXeH%20High%20Temp%20Undercounter%20Dishwasher%20Spec%20Sheet%20F40902%20(09-22).pdf | Codex (needs partner review) | 2026-10-20 | Component-wise medians of 3 filled dishwashing rows (TV-0036, TV-0037, TV-0038): S=1400 W, L=1348.13 W. Equal weight per typical row; component medians need not describe one appliance. Range S=1172.28–1685, L=700–5626 W. Representative source: TV-0037. Broad fallback only; partner review required.
TV-0057 | Any hot-drink appliance | Generic | Used only when no row above fits |  | hot_drinks | 152.5 | 0 |  |  | WHILE_OPEN | In room; generic cannot establish installed heat destination | TV-0041; TV-0065 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Component-wise medians of 2 filled hot_drinks rows (TV-0041, TV-0065): S=152.5 W, L=0 W. Equal weight per typical row; component medians need not describe one appliance. Range S=73–232, L=0–0 W. Representative source: TV-0041. Broad fallback only; partner review required. Only small grinder and cold cooler evidenced; NOT validated for steam-producing espresso/boiling appliances.
TV-0058 | Any electronic device | Generic | Used only when no row above fits |  | electronics | 73 | 0 |  |  | WHILE_OPEN | In room; generic cannot establish installed heat destination | TV-0047; TV-0048; TV-0049; TV-0050; TV-0051; TV-0053 | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Component-wise medians of 6 filled electronics rows (TV-0047, TV-0048, TV-0049, TV-0050, TV-0051, TV-0053): S=73 W, L=0 W. Equal weight per typical row; component medians need not describe one appliance. Range S=22–160.017, L=0–0 W. Representative source: TV-0048. Broad fallback only; partner review required.
TV-0059 | Any sign | Generic | Used only when no row above fits |  | signage |  |  |  |  | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination |  | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. No filled normal-operation sign row exists, so a source-backed generic median cannot be calculated. TV-0052 needs sign size/technology/actual heat. Not replaced with a made-up per-sign wattage.
TV-0060 | Any other appliance | Generic | Used only when no row above fits |  | other | 480 | 0 |  |  | WHILE_OPEN | In room; generic cannot establish installed heat destination | TV-0044 | https://loipart.com/en/product/planetary-mixer-20-l-with-hub-table-type-3810 | Codex (needs partner review) | 2026-10-20 | Component-wise medians of 1 filled other rows (TV-0044): S=480 W, L=0 W. Equal weight per typical row; component medians need not describe one appliance. Range S=480–480, L=0–0 W. Representative source: TV-0044. Broad fallback only; partner review required. Only one dry 20 L mixer is evidenced; especially weak for arbitrary other appliances.
TV-0061 | Pizza deck oven | Any | Confirm number of decks, fuel, dimensions, duty and exhaust. | pizza deck oven;pizza oven;pizza ovens;deck oven;deck ovens | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination |  | https://www.pizzamaster-uk.co.uk/storage/app/uploads/public/696/f4c/59e/696f4c59e0b43608889365.pdf | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. PizzaMaster PM83X sheet p4 publishes normal-operation sensible/latent emissions, but external-hood radiant residual is unspecified and 1–5 decks vary fivefold. No transferable complete free-standing/hooded pair for this unsized type.
TV-0062 | Heat lamp / food warmer lamp | Per lamp | Confirm bulb count, radiant output and retention within room. | heat lamp;heat lamps;food warmer lamp;food warmer lamps;warming lamp | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination |  | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. No sourced normal-service room heat and effective-hood split per lamp found. Rated lamp W is not accepted as measured room heat. Confirm heat output, bulb count and whether lighting already includes it.
TV-0063 | Hot water unit | Under-sink / wall-mounted boiling water | Distinguish boiling-only, stored hot water and boiling/chilled; find model. | HWU;hot water unit;hot water units;boiling water unit;under sink boiler;wall mounted boiler;Zip | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination |  | https://us.zipwater.com/wp-content/uploads/2021/07/802265US-v1.27-06.21-BCS-BCS100-75-Install-Instructions.pdf | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. Zip installation ventilation instructions do not quantify room sensible/latent gain for boiling-only units. Heat exported in drawn water, vented steam, storage loss and cabinet heat must be separated. Do not use element kW.
TV-0064 | Hot food station | Any | Find wells, wet/dry holding, dimensions and hood. | hot food station;hot food stations;hot food display;heated food station | [5 empty] | WHILE_OPEN | Project evidence required: room / exhaust / remote heat destination |  | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. Steam-table and holding-cabinet references are different arrangements; unknown station size, wet/dry state and food throughput prevent a defensible unique value. Use the specified bain-marie/cabinet type when established.
TV-0065 | Water dispenser | Cold bottled water | Sealed cold-water dispenser; exclude hot/boiling and ice dispensing. | water dispenser;water dispensers;water cooler;water coolers;bottled water cooler |  | 232 | 0 |  |  | WHILE_OPEN | Integral air-cooled cold-water cooler in room; no steam |  | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | ASHRAE 2017 ch18 Table 10 top-mounted bottled water cooler: measured peak heat range 114–350 W; midpoint 232 W. Cold-only sealed compressor appliance, latent 0 assumes no steam or open water evaporation. Not a daily average: WHILE_OPEN. Does not cover boiling/chilled systems or ice dispensers. Underlying model identities not published; partner review needed.
TV-0066 | Drinks fridge | Multi-door | Two or more glass doors; integral same-room condenser. | drinks fridge;drinks fridges;beverage fridge;bar fridge 2 door;2DR drinks fridge;multi door fridge |  | 285.833 | 0 |  |  | CONTINUOUS | Integral air-cooled refrigeration in this room; net 24-h heat |  | https://www.bromicrefrigeration.com.au/wp-content/uploads/2023/08/GM1000LWCAS_SPEC_0723.pdf | Codex (needs partner review) | 2026-10-20 | Bromic GM1000LWCAS (960 L, 2 glass doors); manufacturer's Specifications, Energy Consumption (kWh/24h): 6.86. Median of 1 example(s): 285.83–285.83 W; kWh/day ×1000/24. Net room heat equals average electrical consumption for integral same-room refrigeration; NOT condenser gross rejection, cooling capacity or nameplate input. Latent 0: no uncaptured evaporative source. 24-h average, not a compressor peak. Single-product analogue; band not independently validated. Two-door analogue only; 3+-door models may exceed it.
TV-0067 | Outdoor heater | Outdoors — excluded | Outdoor location must be established from the project. | outdoor heater;outdoor heaters;patio heater;patio heaters | [5 empty] | WHILE_OPEN | Outdoors — exclude from indoor room equipment gains |  | https://handbook.ashrae.org/Handbooks/F17/SI/f17_ch18/f17_ch18_si.aspx | Codex (needs partner review) | 2026-10-20 | Further research required if this item is used in the project. EXCLUDED when located outdoors: not an indoor equipment gain. No zero entered. Location/scope exclusion must be applied in the job; this workbook cannot enforce exclusion. An indoor heater requires separate evidence.

## Use patterns
How each item's heat is spread over the day. Every Typical value row names one of these patterns.
Pattern ID | Description | Basis | Fraction of the per-unit heat (blank = the room type's equipment diversity) | Notes
CONTINUOUS | On around the clock | CONTINUOUS | 1 | Self-contained refrigeration. Use only when the per-unit figure is already averaged over compressor cycling; check the source says so.
WHILE_OPEN | On while the room is open | ROOM_HOURS |  | Follows the room's opening hours. Blank fraction uses the room type's equipment diversity from the preliminary pack.